## parameters
| version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.10.1 | TRUE | FALSE |  | 50 | 1

## bus
| name | vn_kv | type | zone | in_service | geo
0 | Bus 0 | 110 | b | CIGRE_MV | TRUE | "{\"coordinates\":[7.0,16.0], \"type\":\"Point\"}"
1 | Bus 1 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 15.0], \"type\": \"Point\"}"
2 | Bus 2 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 13.0], \"type\": \"Point\"}"
3 | Bus 3 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 11.0], \"type\": \"Point\"}"
4 | Bus 4 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [2.5, 9.0], \"type\": \"Point\"}"
5 | Bus 5 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [1.0, 7.0], \"type\": \"Point\"}"
6 | Bus 6 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [1.0, 3.0], \"type\": \"Point\"}"
7 | Bus 7 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [8.0, 3.0], \"type\": \"Point\"}"
8 | Bus 8 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [8.0, 5.0], \"type\": \"Point\"}"
9 | Bus 9 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [6.0, 5.0], \"type\": \"Point\"}"
10 | Bus 10 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 5.0], \"type\": \"Point\"}"
11 | Bus 11 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [4.0, 7.0], \"type\": \"Point\"}"
12 | Bus 12 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 15.0], \"type\": \"Point\"}"
13 | Bus 13 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 11.0], \"type\": \"Point\"}"
14 | Bus 14 | 20 | b | CIGRE_MV | TRUE | "{\"coordinates\": [10.0, 5.0], \"type\": \"Point\"}"

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | load_type
0 | Load R1 | 1 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye | residencial
1 | Load R3 | 3 | 0.27645 | 0.069285 | 0 | 0 | 0.285 | 1 | TRUE | wye | residencial
2 | Load R4 | 4 | 0.43165 | 0.10818 | 0 | 0 | 0.445 | 1 | TRUE | wye | residencial
3 | Load R5 | 5 | 0.7275 | 0.18233 | 0 | 0 | 0.75 | 1 | TRUE | wye | residencial
4 | Load R6 | 6 | 0.54805 | 0.13735 | 0 | 0 | 0.565 | 1 | TRUE | wye | residencial
5 | Load R8 | 8 | 0.58685 | 0.14708 | 0 | 0 | 0.605 | 1 | TRUE | wye | residencial
6 | Load R10 | 10 | 0.4753 | 0.11912 | 0 | 0 | 0.49 | 1 | TRUE | wye | residencial
7 | Load R11 | 11 | 0.3298 | 0.082656 | 0 | 0 | 0.34 | 1 | TRUE | wye | residencial
8 | Load R12 | 12 | 14.994 | 3.0447 | 0 | 0 | 15.3 | 1 | TRUE | wye | residencial
9 | Load R14 | 14 | 0.20855 | 0.052268 | 0 | 0 | 0.215 | 1 | TRUE | wye | residencial
10 | Load CI1 | 1 | 4.845 | 1.5925 | 0 | 0 | 5.1 | 1 | TRUE | wye | industrial
11 | Load CI3 | 3 | 0.22525 | 0.1396 | 0 | 0 | 0.265 | 1 | TRUE | wye | industrial
12 | Load CI7 | 7 | 0.0765 | 0.04741 | 0 | 0 | 0.09 | 1 | TRUE | wye | industrial
13 | Load CI9 | 9 | 0.57375 | 0.35558 | 0 | 0 | 0.675 | 1 | TRUE | wye | industrial
14 | Load CI10 | 10 | 0.068 | 0.042143 | 0 | 0 | 0.08 | 1 | TRUE | wye | industrial
15 | Load CI12 | 12 | 5.016 | 1.6487 | 0 | 0 | 5.28 | 1 | TRUE | wye | industrial
16 | Load CI13 | 13 | 0.034 | 0.021071 | 0 | 0 | 0.04 | 1 | TRUE | wye | industrial
17 | Load CI14 | 14 | 0.3315 | 0.20545 | 0 | 0 | 0.39 | 1 | TRUE | wye | industrial

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | sgen_type | current_source | max_p_mw
0 | PV 3 | 3 | 0.02 | 0 | 0.02 | 1 | TRUE | PV | TRUE | 0.02
1 | PV 4 | 4 | 0.02 | 0 | 0.02 | 1 | TRUE | PV | TRUE | 0.02
2 | PV 5 | 5 | 0.03 | 0 | 0.03 | 1 | TRUE | PV | TRUE | 0.03
3 | PV 6 | 6 | 0.03 | 0 | 0.03 | 1 | TRUE | PV | TRUE | 0.03
4 | PV 8 | 8 | 0.03 | 0 | 0.03 | 1 | TRUE | PV | TRUE | 0.03
5 | PV 9 | 9 | 0.03 | 0 | 0.03 | 1 | TRUE | PV | TRUE | 0.03
6 | PV 10 | 10 | 0.04 | 0 | 0.04 | 1 | TRUE | PV | TRUE | 0.04
7 | PV 11 | 11 | 0.01 | 0 | 0.01 | 1 | TRUE | PV | TRUE | 0.01
8 | WKA 7 | 7 | 1.5 | 0 | 1.5 | 1 | TRUE | WP | TRUE | 1.5

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 7 | 12 | l | CB | FALSE | S2 | 0
1 | 4 | 13 | l | CB | FALSE | S3 | 0
2 | 8 | 14 | l | CB | FALSE | S1 | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max
0 |  | 0 | 1.03 | 0 | 1 | TRUE | 5000 | 5000 | 0.1 | 0.1

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | switch_type | dnr_status | inv_candidate | inv_eur_km | inv_initial_eur | expected_life | discount_Rate | annuatized_cost
0 | Line 1-2 | CABLE_CIGRE_MV | 1 | 2 | 2.82 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 333357.84 | 40 | 0.0558 | 20993.7071 | -20993.7071
1 | Line 2-3 | CABLE_CIGRE_MV | 2 | 3 | 4.42 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 522497.04 | 40 | 0.0558 | 32905.0302 | -32905.0302
2 | Line 3-4 | CABLE_CIGRE_MV | 3 | 4 | 0.61 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 72109.32 | 40 | 0.0558 | 4541.192 | -4541.192
3 | Line 4-5 | CABLE_CIGRE_MV | 4 | 5 | 0.56 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 66198.72 | 40 | 0.0558 | 4168.9631 | -4168.9631
4 | Line 5-6 | CABLE_CIGRE_MV | 5 | 6 | 1.54 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 182046.48 | 40 | 0.0558 | 11464.6485 | -11464.6485
5 | Line 7-8 | CABLE_CIGRE_MV | 7 | 8 | 1.67 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 197414.04 | 40 | 0.0558 | 12432.4435 | -12432.4435
6 | Line 8-9 | CABLE_CIGRE_MV | 8 | 9 | 0.32 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 37827.84 | 40 | 0.0558 | 2382.2646 | -2382.2646
7 | Line 9-10 | CABLE_CIGRE_MV | 9 | 10 | 0.77 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 91023.24 | 40 | 0.0558 | 5732.3243 | -5732.3243
8 | Line 10-11 | CABLE_CIGRE_MV | 10 | 11 | 0.33 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 39009.96 | 40 | 0.0558 | 2456.7104 | -2456.7104
9 | Line 3-8 | CABLE_CIGRE_MV | 3 | 8 | 1.3 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 153675.6 | 40 | 0.0558 | 9677.9501 | -9677.9501
10 | Line 12-13 | OHL_CIGRE_MV | 12 | 13 | 4.89 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | INTERRUPTORT | switchable | no | 58518 | 286153.02 | 40 | 0.0558 | 18020.9131 | -18020.9131
11 | Line 13-14 | OHL_CIGRE_MV | 13 | 14 | 2.99 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | INTERRUPTORT | switchable | no | 58518 | 174968.82 | 40 | 0.0558 | 11018.9223 | -11018.9223
12 | Line 6-7 | CABLE_CIGRE_MV | 6 | 7 | 0.24 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 28370.88 | 40 | 0.0558 | 1786.6985 | -1786.6985
13 | Line 11-4 | CABLE_CIGRE_MV | 11 | 4 | 0.49 | 0.501 | 0.716 | 151.1749 | 0 | 0.145 | 1 | 1 | cs | TRUE | INTERRUPTORT | switchable | no | 118212 | 57923.88 | 40 | 0.0558 | 3647.8427 | -3647.8427
14 | Line 14-8 | OHL_CIGRE_MV | 14 | 8 | 2 | 0.51 | 0.366 | 10.0968 | 0 | 0.195 | 1 | 1 | ol | TRUE | INTERRUPTORT | switchable | no | 58518 | 117036 | 40 | 0.0558 | 7370.5166 | -7370.5166

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | inv_candidate | inv_eur_mva | inv_initial_eur | expected_life | discount_Rate | annuatized_cost
0 | Trafo 0-1 |  | 0 | 1 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [7 empty] | FALSE | 1 | 1 | TRUE | no | 19367 | 484175 | 40 | 0.0558 | 30491.6426
1 | Trafo 0-12 |  | 0 | 12 | 25 | 110 | 20 | 12.0011 | 0.16 | 0 | 0 | 30 | [7 empty] | FALSE | 1 | 1 | TRUE | no | 19367 | 484175 | 40 | 0.0558 | 30491.6426

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
CABLE_CIGRE_MV | 151.1749 | 0.501 | 0.716 | 0.145 | cs
OHL_CIGRE_MV | 10.0968 | 0.51 | 0.366 | 0.195 | ol

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1.03 | 0 | -43.1965 | -15.6962
1 | 0.99413 | -6.0451 | 19.839 | 4.6371
2 | 0.9778 | -6.573 | 0 | 0
3 | 0.95185 | -7.4149 | 0.4817 | 0.20888
4 | 0.95009 | -7.5089 | 0.41165 | 0.10818
5 | 0.94889 | -7.5737 | 0.6975 | 0.18233
6 | 0.94749 | -7.6499 | 0.51805 | 0.13735
7 | 0.9522 | -7.14 | -1.4235 | 0.04741
8 | 0.94919 | -7.4142 | 0.55685 | 0.14708
9 | 0.94826 | -7.4495 | 0.54375 | 0.35558
10 | 0.9471 | -7.5081 | 0.5033 | 0.16126
11 | 0.94692 | -7.5183 | 0.3198 | 0.082656
12 | 1.0001 | -5.4871 | 20.01 | 4.6933
13 | 0.99533 | -5.5382 | 0.034 | 0.021071
14 | 0.99255 | -5.5679 | 0.54005 | 0.25771

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 2.7056 | 1.3044 | -2.6731 | -1.3101 | 0.032492 | -0.0056466 | 0.08722 | 0.087886 | 0.087886 | 0.99413 | -6.0451 | 0.9778 | -6.573 | 60.6113
1 | 2.6731 | 1.3101 | -2.6212 | -1.314 | 0.051931 | -0.0039621 | 0.087886 | 0.088925 | 0.088925 | 0.9778 | -6.573 | 0.95185 | -7.4149 | 61.3278
2 | 1.6314 | 0.38339 | -1.629 | -0.39048 | 0.0023717 | -0.0070903 | 0.050825 | 0.050898 | 0.050898 | 0.95185 | -7.4149 | 0.95009 | -7.5089 | 35.1022
3 | 1.2174 | 0.2823 | -1.2162 | -0.29016 | 0.0012156 | -0.0078537 | 0.03797 | 0.038037 | 0.038037 | 0.95009 | -7.5089 | 0.94889 | -7.5737 | 26.2323
4 | 0.51866 | 0.10783 | -0.51805 | -0.13326 | 0.00060763 | -0.025434 | 0.016116 | 0.016297 | 0.016297 | 0.94889 | -7.5737 | 0.94749 | -7.6499 | 11.2397
5 | 1.4235 | -0.04741 | -1.4188 | 0.025421 | 0.0046772 | -0.02199 | 0.04318 | 0.043157 | 0.04318 | 0.9522 | -7.14 | 0.94919 | -7.4142 | 29.7791
6 | 1.3687 | 0.56951 | -1.3677 | -0.57358 | 0.000979 | -0.0040725 | 0.045085 | 0.045149 | 0.045149 | 0.94919 | -7.4142 | 0.94826 | -7.4495 | 31.1372
7 | 0.82393 | 0.218 | -0.82315 | -0.23002 | 0.0007822 | -0.012019 | 0.025946 | 0.026051 | 0.026051 | 0.94826 | -7.4495 | 0.9471 | -7.5081 | 17.966
8 | 0.31985 | 0.068758 | -0.3198 | -0.074309 | 4.95e-05 | -0.0055515 | 0.0099717 | 0.010009 | 0.010009 | 0.9471 | -7.5081 | 0.94692 | -7.5183 | 6.9028
9 | 0.50812 | 0.72174 | -0.50669 | -0.74201 | 0.0014294 | -0.02027 | 0.026769 | 0.027326 | 0.027326 | 0.95185 | -7.4149 | 0.94919 | -7.4142 | 18.8456
10 | 0.57797 | 0.26917 | -0.57543 | -0.27352 | 0.0025442 | -0.0043506 | 0.018403 | 0.018479 | 0.018479 | 1.0001 | -5.4871 | 0.99533 | -5.5382 | 9.4762
11 | 0.54143 | 0.25245 | -0.54005 | -0.25521 | 0.001377 | -0.0027597 | 0.017326 | 0.017372 | 0.017372 | 0.99533 | -5.5382 | 0.99255 | -5.5679 | 8.9089
12 | 1.4024e-09 | -0.0040931 | 7.808e-14 | -2.2786e-13 | 1.4025e-09 | -0.0040931 | 0.00012471 | 7.3385e-15 | 0.00012471 | 0.94749 | -7.6499 | 0.94749 | -7.65 | 0.086003
13 | 1.1921e-08 | -0.0083466 | -1.2081e-13 | -9.2641e-14 | 1.1921e-08 | -0.0083466 | 0.00025445 | 4.6412e-15 | 0.00025445 | 0.94692 | -7.5183 | 0.94692 | -7.5185 | 0.17548
14 | 4.0442e-09 | -0.0024999 | 2.8077e-14 | -2.7372e-15 | 4.0443e-09 | -0.0024999 | 7.2709e-05 | 8.2046e-16 | 7.2709e-05 | 0.99255 | -5.5679 | 0.99256 | -5.5681 | 0.037287

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 22.5798 | 8.5815 | -22.5446 | -5.9415 | 0.0352 | 2.64 | 0.12309 | 0.677 | 1.03 | 0 | 0.99413 | -6.0451 | 93.808
1 | 20.6167 | 7.1146 | -20.588 | -4.9625 | 0.028695 | 2.1521 | 0.11114 | 0.61126 | 1.03 | 0 | 1.0001 | -5.4871 | 84.698

## res_ext_grid
| p_mw | q_mvar
0 | 43.1965 | 15.6962

## res_load
| p_mw | q_mvar
0 | 14.994 | 3.0447
1 | 0.27645 | 0.069285
2 | 0.43165 | 0.10818
3 | 0.7275 | 0.18233
4 | 0.54805 | 0.13735
5 | 0.58685 | 0.14708
6 | 0.4753 | 0.11912
7 | 0.3298 | 0.082656
8 | 14.994 | 3.0447
9 | 0.20855 | 0.052268
10 | 4.845 | 1.5925
11 | 0.22525 | 0.1396
12 | 0.0765 | 0.04741
13 | 0.57375 | 0.35558
14 | 0.068 | 0.042143
15 | 5.016 | 1.6487
16 | 0.034 | 0.021071
17 | 0.3315 | 0.20545

## res_sgen
| p_mw | q_mvar
0 | 0.02 | 0
1 | 0.02 | 0
2 | 0.03 | 0
3 | 0.03 | 0
4 | 0.03 | 0
5 | 0.03 | 0
6 | 0.04 | 0
7 | 0.01 | 0
8 | 1.5 | 0

## res_switch
| i_ka | loading_percent
0 | 0.00012471
1 | 0
2 | 0
3 | 0.00025445
4 | 0
5 | 7.2709e-05
6 | 0.12309
7 | 0.11114

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | sgen | name | object
16 | sgen | bus | int64
17 | sgen | p_mw | float64
18 | sgen | q_mvar | float64
19 | sgen | sn_mva | float64
20 | sgen | scaling | float64
21 | sgen | in_service | bool
22 | sgen | type | object
23 | sgen | current_source | bool
24 | switch | bus | int64
25 | switch | element | int64
26 | switch | et | object
27 | switch | type | object
28 | switch | closed | bool
29 | switch | name | object
30 | switch | z_ohm | float64
31 | switch | in_ka | float64
32 | ext_grid | name | object
33 | ext_grid | bus | uint32
34 | ext_grid | vm_pu | float64
35 | ext_grid | va_degree | float64
36 | ext_grid | slack_weight | float64
37 | ext_grid | in_service | bool
38 | ext_grid | s_sc_max_mva | float64
39 | ext_grid | s_sc_min_mva | float64
40 | ext_grid | rx_min | float64
41 | ext_grid | rx_max | float64
42 | line | name | object
43 | line | std_type | object
44 | line | from_bus | uint32
45 | line | to_bus | uint32
46 | line | length_km | float64
47 | line | r_ohm_per_km | float64
48 | line | x_ohm_per_km | float64
49 | line | c_nf_per_km | float64
50 | line | g_us_per_km | float64
51 | line | max_i_ka | float64
52 | line | df | float64
53 | line | parallel | uint32
54 | line | type | object
55 | line | in_service | bool
56 | trafo | name | object
57 | trafo | std_type | object
58 | trafo | hv_bus | uint32
59 | trafo | lv_bus | uint32
60 | trafo | sn_mva | float64
61 | trafo | vn_hv_kv | float64
62 | trafo | vn_lv_kv | float64
63 | trafo | vk_percent | float64
64 | trafo | vkr_percent | float64
65 | trafo | pfe_kw | float64
66 | trafo | i0_percent | float64
67 | trafo | shift_degree | float64
68 | trafo | tap_side | object
69 | trafo | tap_neutral | float64
70 | trafo | tap_min | float64
71 | trafo | tap_max | float64
72 | trafo | tap_step_percent | float64
73 | trafo | tap_step_degree | float64
74 | trafo | tap_pos | float64
75 | trafo | tap_phase_shifter | bool
76 | trafo | parallel | uint32
77 | trafo | df | float64
78 | trafo | in_service | bool
79 | res_bus | vm_pu | float64
80 | res_bus | va_degree | float64
81 | res_bus | p_mw | float64
82 | res_bus | q_mvar | float64
83 | res_line | p_from_mw | float64
84 | res_line | q_from_mvar | float64
85 | res_line | p_to_mw | float64
86 | res_line | q_to_mvar | float64
87 | res_line | pl_mw | float64
88 | res_line | ql_mvar | float64
89 | res_line | i_from_ka | float64
90 | res_line | i_to_ka | float64
91 | res_line | i_ka | float64
92 | res_line | vm_from_pu | float64
93 | res_line | va_from_degree | float64
94 | res_line | vm_to_pu | float64
95 | res_line | va_to_degree | float64
96 | res_line | loading_percent | float64
97 | res_trafo | p_hv_mw | float64
98 | res_trafo | q_hv_mvar | float64
99 | res_trafo | p_lv_mw | float64
100 | res_trafo | q_lv_mvar | float64
101 | res_trafo | pl_mw | float64
102 | res_trafo | ql_mvar | float64
103 | res_trafo | i_hv_ka | float64
104 | res_trafo | i_lv_ka | float64
105 | res_trafo | vm_hv_pu | float64
106 | res_trafo | va_hv_degree | float64
107 | res_trafo | vm_lv_pu | float64
108 | res_trafo | va_lv_degree | float64
109 | res_trafo | loading_percent | float64
110 | res_ext_grid | p_mw | float64
111 | res_ext_grid | q_mvar | float64
112 | res_load | p_mw | float64
113 | res_load | q_mvar | float64
114 | res_sgen | p_mw | float64
115 | res_sgen | q_mvar | float64
116 | res_switch | i_ka | float64
117 | res_switch | loading_percent | float64